Growth and Regeneration: Transport, Traffic and Highway Maintenance

Bristol City Council Procedure for the Approval, Installation, Operation and Maintenance of Illuminated Seasonal Decorations on or above the Public Highway

| Contents 1.0 Introduction and General Background 2 2.0 Health & Safety 5 3.0 Proposed Procedure for Approval of Seasonal Illuminations Over the Highway 7 4.0 General Requirements 9 5.0 Structural Requirements 11 6.0 Electrical Requirements 12 7.0 Electricity Consumption & Un-metered Supply Agreement 14 8.0 Bristol City Councils MPAN & Meter Administration Service 15 9.0 Traffic Management Requirements 17 10.0 Inspections 17 LIST OF APPENDICES 19 |  |  |
| --- | --- | --- |

## 1.0	Introduction and General Background

1.1	Whilst recognising the pleasure a well-designed lighting display gives to the public, organisers and installers of festive lighting must keep in mind that such installations, when powered by mains electricity, are, because of their temporary nature, potentially hazardous. It must be remembered that outdoor lighting is subject to adverse weather conditions, especially in winter, and a hastily erected display could easily bring tragedy instead of joy.

1.2	The fundamental aim of any illuminated festive decoration is to provide a brighter and more interesting environment at night, creating an atmosphere that makes the location special for the occasion. The day time appearance of the decoration is, however equally important and both aspects should be considered at the design stage. Festive decorations can take various forms, a number of which are listed below:

- Simple festoon with multi-colored light sources;

- Decorations mounted on poles or columns;

- Area spanning decorations mounted on catenary wire attached either to buildings or poles;

- Ground Mounted Features;

- Christmas Trees and other static or mobile features;

- Additional Effect Lighting;

- Laser Displays

- Projected Displays from a remote location;

1.3	For clarification and by definition Seasonal or Festive decorations/illuminations are defined as any decorations, supports, fixtures, electrical lighting and associated wiring and fixing ties etc. that are to be installed to celebrate a particular event, which is contained within curtilage of the Adopted Highway.  The licence will apply to the road name to which the installation is being erected and other proposed installation(s) on a different road(s) will require a separate licence(s).

1.4	Therefore any Promoters and Operators wishing to install Seasonal or Festive decorations or illuminations, must gain the full approval of Bristol City Council (as the TAA) as part of their planning, consultations and licence application submission in accordance with Section 178 of the Highway Act 1980 – Restrictions on placing apparatus etc. over Highways.

1.5	The permission of the person(s) or organisation(s) responsible for the land over which, or adjacent to where the decorations/illuminations are proposed to be installed must also be obtained well in advance of the installation works commencing. The minimum timeframe is 12 weeks minimum from commencement onsite; no applications will be considered outside of this time frame. Similarly the permission of the building(s) owner(s) to which the installations are to be attached must be sought and received well in advance of the installation works commencing, please note that way-leave agreements and listed building consent will also be the responsibility of the installer and no permit will be granted unless documentation proof can be provided at the time of making the application.

Note: Not all roads and footpaths are dedicated as Adopted Highways and may be privately owned or public realm land, likewise these permissions must be sought separately.

1.6	If the installation is to be attached or secured to a Listed Building or structure, the person(s) or organisation(s) responsible for the festive lighting application submission will also need to 	make a separate Listed Building Consent application. This Listed Building consent can be 	found on the BCC Planning Application portal at:

https://www.bristol.gov.uk/planning-and-building-regulations/apply-for-listed-building-consent

Please include one of 	the Listed sites as the main address for the application and then list all 	the other sites in the details section – property number, name of road and postcode.

The Institution of Lighting Professionals have produced a Code of Practice (CoP) for the    Installation, Operation and Removal of Seasonal Decorations (Second Edition) and a guidance document (PLG06), Guidance on Installing and maintenance of Seasonal Decorations and Lighting Column Attachments, which are available via:

The Institute of Lighting Professionals

Regent House

Regent Place

Rugby

CV21 2PN				Tel: 01788 576492

This CoP, is intended to provide essential guidance to any person/s engaged in or associated with the installation, operation and maintenance of illuminated seasonal decorations on or above the public highway.  The CoP covers:

- Structural Requirements

  - General overall Requirements including proposed installation Dates and date of Tests

  - Cross-road decorations and festoon decorations

  - Load Calculations and pull out test requirements

  - BCC Structures Engineers to be informed of a recent date of a Pull Out Test and if necessary contacted so we can observe and verify this structural aspect

  - Permanent Infrastructure

  - Anchorage & Catenary wire inspection & testing

- Electrical Requirements

  - General

  - Authorisation

  - Decorations

  - Wiring

  - Maintenance Arrangements

  - Supplies and Energy

- Traffic Management

- Other Requirements

  - Insurance

  - License Applications

  - Aesthetics

1.7	The CoP is being adopted by Bristol City Council as the basis for a minimum standard technical reference document for any proposed licence application submission and thus the application will be dealt with in accordance with Section 178 of the Highway Act 1980. The CoP and the recommendations contained therein, will be used as the minimum standard template for the application as this CoP is based on good, sound engineering judgement and practice, with specific clauses contained in this document taking further precedence.

1.8	The CoP does not in any way constitute a comprehensive specification and as such does not cover all associated operations and activities. It serves to identify only those operations and activities associated, that may, directly or indirectly affect electrical safety or safety to the Highway users and as a supplement to all other existing Codes of Practice, safe working methods and other statutory regulatory requirements. However, the specification clauses contained within this document will take precedence over any other documents, with the CoP being used as a minimum standard to work to. The Body or Contractor must comply fully with this specification and with the CoP.

1.9	For any proposed permanent lighting installations/arrangements over an Adopted Highway a further additional Statutory Licence will be required to install in the general space above the highway, (over sailing Licence – Section 177 – 1980 Highway Act).  Details of this separate licence will be available on request.

## 2.0	Health & Safety

2.1	Whoever instigates the erection & removal of the Festive Decorations, be it an Approved Contractor, Council Organisation, Chamber of Commerce, Street Traders etc. That body assumes all responsibility for Health and Safety whilst working on the Contract and employs or has employed a Skilled and Competent Person(s). The body must ensure all of the Decorations are fit for purpose, correctly supported, electrically safe and as such do not present a potential hazard to the public. The Local Authority will monitor and inspect all aspects of the work, refer to Section 10. If at any time should the Appointed body/Contractor be in breach of this specification, work will be suspended with immediate effect until the body/Contractor has satisfied the Local Authority of compliance.

2.2	The Body/Contractor must comply with the requirements of the Construction Design and Management Regulations 2007, CDM, whilst the works are not themselves notifiable, the installations are temporary in nature and present a risk within the highway, the design, construction and removal must be approached correctly and all risks identified and managed.

2.3	The Contractor must take reasonable steps to ensure that the organisation or individual they propose to appoint with regard to installation, maintenance and operation of the festive lighting is competent. This applies to any party involved within the design (concept, feasibility through to detailed design), specification and construction process of temporary or permanent works.

2.4	The competency of the Contractors proposed staff will be assessed by the Authorities nominated “Skilled Electrical Person” as defined by the IEC and BS7671 18th Edition. Anyone carrying out Electrical Works, must be classed as “Skilled Electrical Person” and therefore to avoid any doubt graded as an Electrician as set out by the JIB and hold an ECS card as a graded Electrician. Non-Electricians are not permitted to carry out any electrical works on the network in any shape or form.

The Contractor shall also as a minimum competency requirement, anyone associated with the works onsite shall be taken as registration of the organisation and staff to the Highway Electrical Registration Scheme (HERS) and where ISO 9001 is required, to National Highway Sector Scheme NHSS 8. This will not override the requirement for all electrical works to be carried out by a qualified Electrician.

2.5	The appointed Contractor must be a member of the Association of Street Lighting Electrical Contractors (ASLEC) with a minimum of all staff employed on the works being registered with an appropriate sector competence scheme specific to highway lighting, as detailed above and have a qualified/registered Electrician carrying out all electrical works. Only Electrically Skilled and Electrically Instructed Personnel as defined by the ICE and BS7671 18th Edition shall be employed in the installation, operation, maintenance or removal of any equipment, with electrical connections/Testing by qualified Electricians only. All staff must have acquired a G39 certificate, the certificate be within the date ranges, not expired and be able to demonstrate competency in this subject.

2.6 	Those accepting the festive lighting commission are reminded that no duty holder must accept an appointment unless they are competent to undertake the work and fully comply with this document and the specification clauses contained within. No unregistered organisation shall undertake any electrical work in relation to any festive decorations. The Contractor must provide a full and detailed document, showing who will be the Duty Holder, listing their qualifications and selection criteria. A family tree showing the chain of command, the operatives names, relevant skill sets/qualifications and roles and responsibilities. This information must be provided prior to any works starting onsite

2.7 	A Contractors H&S plan complete with copies of competencies, specific method statements, risk assessments, Duty Holder details and family tree as detailed in 2.6 must be submitted to the Authorities “Skilled Electrical Person for approval prior to any work starting on site. Any member of staff working on the festive lighting who has not submitted training records will be removed from the work at the Clients/Contractor expense. Specific method statements, time period, risk assessments, designers risk assessments, product information etc, must be submitted and approved prior to any works starting on site.

2.8	The Contractor must ensure all staff and Management systems comply with the Health and Safety at Works Act1974, Management of Health and Safety at works act 1992 & 1999.

2.9	If the Contractor elects to use sub-contractors then the same clauses above and contained in this document will apply to the sub-contractors.

3.0	No Contractor or Sub-Contract will be allowed to start work unless the requested information is provide and then approved by the Authorities “Skilled Person”. No exceptions will made.

## 3.0	Proposed Procedure for Approval of Seasonal Illuminations Over the Highway

3.1	All applications and installations for any Seasonal illuminations over the Highway shall comply with the following:

- BS7671 18th Edition Wiring Regulations

- County Surveyors Society COP “For the Installation, operation and Removal of Seasonal Decorations”

- Electricity at Work Regulations 1989

- Health and Safety at Works Act 1974

- Management of Health and Safety at Works Act 1992 & 1999

- New Roads and Street Works Act

- Highways Act 1980

- PLG06 Guidance on Installation and Maintenance of Seasonal Decorations and Lighting Column Attachments

3.2	No seasonal illumination, cables, supports or other attachments are to be fitted to any Highway Authority apparatus without the prior written consent of the Highway Authority. Such consent would be in the form of a formal Licence application submission in accordance with Section 178 of the 1980 Highway Act, and would require any Commissioner/Promoter to ensure that he/she has satisfied the Council requirements. The Licence is included in Appendix “B”.

3.3	The licence application should in the first instance be submitted to the Bristol City Council (BCC) Street Lighting Representative, who will ensure initially that the licence application compiles fully with the Council general requirements conditions which are set out in this document.

3.4	BCC Street Lighting Representative will also ensure that the licence application submission contains the following supporting information before it can proceed and be processed:

- Completed Licence application form (SL1). Refer to Appendix A.

- Copy of the relevant Insurance Certificate(s) (Public Liability, professional indemnity).

- H&S details, Construction H&S Plan, Risk Assessments, Method Statements, Qualifications/Competencies, family Tree detailing chains of command, Duty Holder details.

- Detailed Drawing in AutoCAD or Similarly Approved (Not hand Drawn) showing the Highway(s) to which the illumination are to be erected, the route of lighting span, the fixing locations, the electrical control points feeding the installation. If attached to lighting columns, the column ID (Including all decorations clearly identified with and unique “id” number. The Drawing should have a key, clearly identifying types of equipment, drawings shall be numbered, initials drawn by, initials checked by and dated. (PDF example shown on Appendix C).

- Simple Circuit Chart for all connected circuits (PDF example shown on Appendix C).

- Typical elevation(s) showing the arrangement of the proposed installation(s).

- The schedule of proposed labelled anchorage attachment fixing points to building(s) or structure(s), the Council operates a “scafftag” system. (PDF example shown on Appendix D1)

- Copy of any Structural Engineer’s Reports on fixing arrangements and calculations (If appropriate).

- Copy of the up to date Anchorage and Catenary Wire Register.

- Anchorage Load Pull out Tests Result (this must be a recent test and be inside the permitted date ranges)

- Schedule of attachment location, Supply Isolation points, Circuit Protection Details, (Appendix D2).

- Electrical Testing& PAT Certificates once energised (Not required at application stage). (Appendix E).

- Copy of Written Energy Agreement with Meter Administrator (WPD) & detailed breakdown of Equipment, burning times and loadings to enable calculation of energy usage, (Appendix F).

- Form F1 if the scheme organiser wants the Authority to act as meter administrator + payment to cover fees to act as Meter Administrator.

- Where the scheme organiser wants to use the Authority as a Meter Administrator then an additional cost  will be charged Subject to the size and complexity of the display + the cost of the electricity consumption, which will be calculated when Appendix F is received. (Please Refer to clauses 8.0 to 8.6 of this Specification)

- Name and Contact Details of Duty Holder, Installer/Lighting Contractor/Sub Contractor, plus “Out of Hours” contact list, including a in and out of hours number for a 2-hour response in the case emergencies.

- For new festive lighting proposals a fee of (£2,889 & Vat), will be charged to cover the costs associated with the preparation and implementation of the licence (legal and engineering aspects).

- For existing schemes which have previously been approved by BCC, and 50% reduction (£1,444 & Vat) of the fee shall be charged, subject to this being fully checked and approved by BCC Engineers. The extent of change from the previous installation my warrant the fee to be increased as appropriate.

3.5	The Bristol City Council (BCC), Lead Officer will then ensure that the relevant submitted information is issued to the relevant Council Officer for examination and Approval of their technical element of the licence requirements. The relevant Council Officers will be within the following disciplines:

Street Lighting					Electrical Requirements

Bridges and Highway Structures			Structural Requirements

Network Management					Traffic Management Requirements

Legal Services						Insurances and Licence Agreements

3.6	If the technical requirements of the submission have been reached the Officers responsible for the above four discipline’s will inform the BCC Street Lighting Representative if technical compliance for their individual element of the approval has been achieved and that the licence application can proceed with BCC Legal Services.

3.7	The BCC Street Lighting Representative will then arrange for the compilation of the new Licence under Section 178 of the Highways Act, ensuring that all technical requirement section of the licence have been signed and dated by all the relevant Council Officers.

3.8	The BCC Street Lighting Representative will arrange for completion of the Licence and will organise the final signing and dispatch of this licence to the Licensee.

3.9	If for any reason the Licensee is rejected the BCC Street Lighting Representative will inform the person or persons submitting the proposal in writing detailing exactly the reason why the submission has been rejected.

3.10 	It is the Licensee obligation to consult with the various other arms of the Council and outside organisations, such as the following:

- Permission under Town Planning, Historic Listed Buildings and Advertisement Regulations

- Tree Team.

- Special Events authorisation Permits . – BCC Site Permissions

- Avon and Somerset Police.

- BCC CCTV Operations.

- Necessary Permission from Adjacent Private Building or Landowners.

## 4.0	General Requirements

4.1	Illuminations and/or their supports will not project within 0.5m of the kerb edge and at no less a height than 5.7m above the carriageway. Where roads within the Authority have been designated “Wide Load Route” a minimum clearance of 7.5m above the carriageway surface must be maintained at all times.

4.2	Illuminations and/or their supports erected over the footways/s and any other pedestrian areas, must maintain a minimum clearance of 3.5m from the footway surface.

4.3	No permanent fixtures are to be fitted in or attached to any Highway Authority street furniture or other property without the prior written consent of the Authority.

4.4	The drilling of fixture access holes into existing columns will not be permitted without prior permission from the BCC Street Lighting Representative. Any existing pre-existing access fixture holes must be suitably sealed and weather proofed against corrosion.

4.5	No attachment is to be made to any bracket arm or extension fitted to a lighting column or traffic sign without the specific approval of the highway authority. General approval will not be given to the attachment of illuminations to the following substrates:

- Concrete, cast iron, aluminium or GRP columns.

- Traffic Signs

- Traffic Signal Posts

4.6	The Operator will be held responsible for any damage to the painted finish, galvanising or other protective coating systems to any highway apparatus used in the installation.

4.7	No illumination shall interfere with or obstruct access to the columns or lanterns in the course of general/cyclic maintenance activities. No illuminations shall be fitted to lighting columns that already support existing attachments such as traffic signs, signals, CCTV cameras other than a “small” sign plate not exceeding 0.03 m2.

4.8	Approval for attachments will only be given when the Operator has demonstrated by proper testing and submission of suitable and acceptable load calculations that the structural integrity of the apparatus to which the attachment are to be made will not be compromised.

4.9	The full cost of the required structural testing will be carried out at the Operators expense.

4.10	The owner of the equipment must at his own expense, maintain the equipment in good repair during installation, operation and until the equipment is removed. The Festive Lighting installer must provide the BCC Street Lighting Representative with a manned phone number to provide a 24 hour 7 days per week response with a 2-hour response time to any dangerous on site situation involving the festive decorations or associated equipment. No license will be granted unless the Contractor can demonstrate compliance with this clause. Details of the emergency response staff competences will be required prior to granting approval.

4.11	The Highway Authority has the right to disconnect and remove any or all equipment, which in its opinion is unsafe or dangerous to the general public.  The cost of this work is rechargeable to the equipment owner and will be charged by using day work rates.

4.12	The requirements for signing at Roadworks, detailed in Chapter 8 of the Traffic signs Manual shall be observed at all times when installing, maintaining or removing the decorations. All traffic management operations must be submitted in writing to the BCC Network Management team and agreed prior to starting on site. A vast majority of roads in the city centre and traffic sensitive and will require out of hours working.

4.13	No individual festive lighting circuit will consume a total load of more than 500W – If such a circuit is proposed then applicant will require an electric meter to measure the total power consumed and to liaise with Local Electricity Company (Western Power Distribution).

4.14	The Contractor will be required to operate an out of hours and in hours 2-hour response to any call from Bristol City Council to attend site and make safe a reported situation. Failure to attend site within the two-hour time scale, not answering the initial call or leaving/ignoring a dangerous or potentially dangerous situation will result in the Bristol City Council having no other option than to call its Term Maintenance Contractor and Street Lighting Officer to deal with the issue.

The cost of this will be recharged back as per below:

- Initial Call Out Charge £300 (Term Contractor & Street Lighting Officer)

- Extra Over Initial Hour attendance £105 per hour

4.15	No organisation other than Bristol City Councils Term Maintenance Contractor is permitted to install new power supplies onto the lighting network. These works, materials and officers time will be charged back to the operator using the current Term Maintenance Contract Rates and materials base costs plus 15%. The operator must submit details of new supplies with any application and the BCC Street Lighting Representative will provide the organisation with a detailed quotation

Street Lighting Contacts Details

Mr. Steven Thomas				steven.thomas@bristol.gov.uk

Mr Rory McGrath				rory.mcgrath@bristol.gov.uk

## 5.0	Structural Requirements

5.1	All proposed illuminated seasonal decorations on or above the highway shall be installed in accordance with the Code of Practice for the Installation, Operation and Removal of Seasonal Decorations – Section 2 – Structural Requirements.

5.2	Any cable spans greater then 3m are to be supported by means of a high tensile steel galvanised/stainless steel, multi strand, catenary wire, of a minimum diameter of 6mm. The support cable be either continuously interwoven with the catenary wire, or secured to the catenary wire, by means of suitable clips/cable ties at no greater than 250mm centres throughout its length.  Catenary wire may also be integral to the cable as part of the production process.

5.3 	The catenary wire must be securely attached to an approved anchorage point, which has been tested in accordance with the CoP. No cross road spans of catenary lights or bunting are to be fixed to lighting columns, as it is not usually possible to achieve the minimum 5.8m (7.5m on abnormal load routes) height clearance in the middle of the span due to cable sag. All catenary cables must have a unique identification number attached to the catenary and be recorded on the as built drawings.

5.4	All anchorage points/bolts/hooks/design fixing brackets/cable tensioners must be made of non-corrosive material such as galvanised/stainless steel and must be designed for the purpose and to BS5649 classification - part 6. All brackets/clips shell be fitted with neoprene rubber insert of minimum 5mm thickness, between the column and the fixing.

5.5	The Operator/Promoter shall ensure that the design of, and construction of, any street lighting illuminations, including fixings and anchorage points comply fully with the requirements of BS5649 – Part 6 and also the CoP.

5.6	A schedule list and drawings of proposed locations with approved and tested and clearly labelled anchorage points would then be included on a Council Approved list of proposed anchorage points. This approved list(s) and drawing(s) could then be distributed to any promoter of festive illuminations for their use in proposing and future scheme proposal for Council Approval.

5.7	All anchor fixings are to incorporate a “scafftag” system, with all anchor points having a unique identification number and a record of all fixings submitted with the application.

Structural Engineering Contact Details

Completed Licence applications to be emailed to the following Address:

Bridgeshighwaystructures.ta@bristol.gov.uk

## 6.0	Electrical Requirements

6.1	All displays requiring connections shall ensure that all decorative features or equipment have been constructed, and shall be installed, maintained and operated, in full compliance with the current editions of:-

- ILP Code of Practice for the Installation, Operation and Removal of Seasonal Decorations – Section 3 – Electrical Requirements.

- PLG06 Guidance on Installation and Maintenance of Seasonal Decorations and Lighting Column Attachments.

- BS 7671 Institution of Electrical Engineers Regulations for Electrical Installations.

- Code of Practice for Electrical Safety in Highway Lighting Operations.

- The Electricity Supply Regulations.

- The Electricity at Work Regulations 1989.

- The Construction (Design and Management) Regulations 2007.

- Unmetered Supply agreement

- G39 Works involving Street Furniture

- New Roads and Street Works Act (NRSWA)

6.2	Approved Contractor - Festive Lighting works will usually be linked to electrical equipment owned by the City Council. Any Contractor must reach the criteria set out in clause 2.4 ,2.5, 2.6 and be a member of the Association of Street Lighting Electrical Contractors (ASLEC). Only Electrically Skilled and Instructed Skilled Electrical as set out by the ICE and BS7671 personnel shall be employed in the installation, operation, maintenance or removal of any equipment, with qualified Electricians only carrying out Electrical works and Electrical Testing (see specific clause regarding testing 6.9) . All staff must have acquired a G39 certificate. Copies of staffs competencies along with specific method statements and risk assessments, must be submitted to the BCC Street Lighting Representative for approval prior to any work starting on site. Only qualified electricians are allowed to work on the electrical system.

6.3 	The electrical installation must be installed to the same standards as a permanent installation although it is appreciated that for an installation of this nature cables maybe installed in a temporary manner. Cable supports must be so arranged that there is no appreciable mechanical strain on any cable termination or joint as per BS7671.

6.4	Where new electrical supplies via the Councils existing Street Lighting system are required, all works must be carried out by Bristol City Councils Term Maintenance Contractor and supervised by the BCC Street Lighting Representative. All works and materials will be re-charged back to person or persons responsible for the event and payment in advance of works will be required, subject to the BCC Street Lighting Representative producing a detailed quotation.  All Electrical installations carried out, which are intended for connection to the street lighting system, must comply in every respect with BS 7671 and supplementary protection by the use of a BCC approved combined Specific Festive Lighting isolator, with a 16A RCBO, BS88 fuse and Digital timing unit, combined in a waterproof unit, suitable for mounting inside a Lighting Column, feeder pillar or IP67 wall box. Only this unit can be used with an approved Commando Style IP67 Socket Outlet for all Festive Decorations.

6.5	All plugs, sockets and connectors shall comply fully with BS EN 60309-2:1998 and shall have an IP rating of not less than IP 67 according to BS EN 60529:1992 unless housed within a weather-proof enclosure with an IP rating of not less than IP 67.

6.6 	If the Contractor wishes to propose an alternative manufacturer to the one specified by the Lighting Engineer, then the alternative product must be equal to or greater in quality than that specified. The Authority reserves the right refuse alternative equipment. The Contractor will be asked to submit detailed information about the product and schematic wiring diagrams.

6.7	Any electrical cables less than 3.5 metres above ground level shall be fully enclosed in a high impact plastic or heavy-duty galvanised steel conduit securely fixed to a solid structure. Where the conduit is fixed to a lighting column it shall be secured by means of 15 mm stainless steel ‘Bandit’ tape and buckles at centre no greater than 1000 mm. All steel conduits shall be effectively connected to earth.

6.8	Decorative features may be connected to individual lighting columns and will be supplied at mains voltage only if the heights and clearances can be achieved. Electrical design and loading must be such as to ensure the safe operation of the decorations in all circumstances and in every case must be approved by the BCC Street Lighting Representative.

6.9	Each Year as the electrical supplies are energised, the Contractor must carry out a full electrical tests and visual inspection on all power supplies used in relation to the festive lighting installation. This must also include testing all the temporary cables and fixed power supplies feeding the decorations and shall be carried out in accordance with BS7671 and as specifically itemised in Section 17 of the Institute of Lighting Employers Code of Practice for Electrical Safety in Public Lighting Operations.  The Tests must be carried out by an Electrician who is qualified to C&G 2394/95 or C&G 2391/52.  Final Electrical Test certificates with test results for each circuit from each Supply Point shall be sent to the BCC Street Lighting Representative the next working day of circuit being energised in pdf format, emailed to steven.thomas@bristol.gov.uk. Calibration certificates of any test equipment used, must also be provided with the test certificates. Any breaches of electrical safety found onsite, must be reported immediately and made safe. A sample Electrical test certificate is included within Appendix “E”. If the Contractor wishes to use a different test certificate then the Contractor must have the test certificate authorised by the Authority.

Note: Please be aware each test certificate must be uniquely numbered and be signed by the tester, who shall be authorised and a qualified Electrician. The test certificate must be countersigned by the appointed person within the organisation.

6.10	Each year the decoration(s) and associated cabling/controls connected directly to decoration must be visually checked and electrical tested prior to the erection of the decoration, each year. This will be in the form of a PAT test as recommended by BS7671 and the relevant publications listed in clause 6.1The results and evidence of the testing procedure must be given to the authority no later than one working day after the decoration is switched on.

6.11	All electrical supplies feeding the decorations, must be protected by a RCD/RCBO as detailed in BS7671. If the device is not present then the circuit shall not be energised. All electrical tests to include an RCD/RCBO test as detailed in BS7671.

6.12	Failure to provide the test results by the prescribed timescales will almost certainly lead to the displays being switched off until the test certification is received. The costs for switching the supplies off will be charged back to the Contractor at a rate of £105 per hour. The re-witching on of the decorations will be carried out by the Contractor and all costs associated with this absorbed by the Contractor.

6.13	Power supplies to decorative festive lights should not be derived from adjacent buildings, but from within the street lighting column acting as the support. (This is to avoid instances of connection to private supplies, over which the Highway Authority or its Agent has no control.

## 7.0	Electricity Consumption & Un-metered Supply Agreement

7.1	90% of all the electrical supplies associated with the Street Lighting electrical supply are via WPD unmetered supplies, there are some supplies via a metered supply, but this is minimal. Any body or operator proposing to connect their equipment into the system must first gain permission via WPD and obtain an agreement in the form of a un-metered supply agreement specifically for Festive Lighting, with a specific MPAN number, an example of this document is shown in Appendix “F”.

7.2	The body or promoter must provide the Meter Administrator (WPD) with a list of all decorations connected to the un-metered power supply. A comprehensive list will be required in a format specified by WPD and as per the example in Appendix “F”. Failure to provide the list and proof of WPD authorisation prior to the circuits being energised will result in the electricity being switched off with immediate effect and the costs to carry this out will be charged back to the body or promoter.

7.3	The body or promoter responsible for the installation/connection of the decorative lighting shall, separately, contract with an electricity supply company for the supply of energy. It is strongly recommended that early talks with WPD regarding this matter be taken up. There are several potential financial, legal and safety issues that may arise, were the City Council permits a third party to make (or arrange to have made) temporary connections to lighting equipment without the permission of the Electricity Company and will certainly result in a fine and the display being disconnected form the electrical network , as mentioned previously in clause 7.2.

7.4	The Council will not pay for any electricity used as a result of the Festive Lighting. It is the body or promoter’s obligation to pay for any electricity used and legal action will most certainly be taken against non-payment to reclaim the monies owed and cover any other losses associated with an illegal connection to the electricity supply

7.5	If you make an unauthorised connection, to the councils street lighting unmetered assets, for example without a valid MPAN number, your organisation will be liable to prosecution for the theft of electricity and will face legal action for any costs suffered as a result.

7.6	WPD are the meter administrators and the point of contact to obtain a specific Festive Lighting Unmetered Supply agreement and ultimately gain permission to connect into the WPD network.

WPD Contact Details:

Mr. Brian Newberry

Unmetered Supplies Manager

Western Power Distribution

Tel: 01392 352667

## 8.0	Bristol City Councils MPAN & Meter Administration Service

8.1	Bristol City Council recognises the issues and possible complications around organising the MPAN and appointing an energy supplier. As a result, Bristol City Council offer the service to event promotor and organisers.

8.2	If the organiser wishes to use Bristol City Council MPAN number to trade electricity and use the Bristol City Councils Meter Administrator, then a charge for this service will be applied extra over top the license fee. The cost of the service will be subject to the size of the display and the number of decorations installed.

8.3	The organiser must complete the form in Appendix G and include this information with the initial submission. This information will be used to calculate both the Energy Costs and the Administration Costs. Once calculated the Authority will email the organiser with a quotation and energy consumption costs based on the following data:

8.4	The method of how final unmetered supply electrical usage settlements are calculated with the meter administrator, uses specific switch on and off times as set out by UMSUG. Therefore, the event switch on and off times must mirror one of the switching events as set out by UMSUG and as included in Appendix “G” C/W Examples. The Contractor must set the switch on and off times at each location to a valid switch regime.

- Electrical Loadings in KW of each decoration;

- Switch on Date;

- Switch on and off daily times;

- Switch off Date;

8.5	Payment of Electricity Consumption and Payment of the Administration Costs must be paid in advance of the display being switched on.

8.6	If for any reason the electricity consumption is greater than the originally submitted, calculated/forecast consumption, then the Authority will retrospectively invoice for the additional costs, including additional Administration costs.

Reason can be, but not limited to the following:

- Decorations not switching on & off at the prescribed times

- Change of Switch on and Off Dates

- KW Load information not correct

8.7	The Authority intends to sample audit installation and record power information and switching times of the decorations to ensure the data provided is in line with the data onsite and therefore satisfy the UMSUG rules.

8.8	If you make an unauthorised connection, to the councils street lighting unmetered assets, without a valid MPAN number or a contract in place with the Authority to act as your meter administrator, your organisation will be liable to prosecution for the theft of electricity and will face legal action for any costs suffered as a result.

8.9	Switching on and off times will be as per the Switching times agreed by UMSUG.

8.10	Failure to de-energise the circuit by the prescribed time will result in additional costs to the event.

## 9.0	Traffic Management Requirements

9.1	Any works on the Highway will need to be actioned using the permit scheme, as detailed in the link below:

https://www.bristol.gov.uk/licences-permits/roads-and-highway-licences

No works will be allowed on the Bristol City Council network without a valid permit

9.2	All proposed illuminated seasonal decorations on or above the highway shall be installed in accordance with the Code of Practice for the Installation, Operation and Removal of Seasonal Decorations – Section 4 – Traffic Management Requirements and the New Roads and Street works Act, known as NRSWA.

9.3	All staff employed on the Festive Lighting Contract shall have a NRSWA qualification and one member of staff will be qualified to Supervisor level.

9.3	Specific traffic management operations as a result of the works or in conjunction with the works must be submitted and discussed further with BCC Network Management and agreement must be sought prior to any work start on site.

9.4	Prior to installation, all traffic management must be agreed in writing with BCC Highway Network Management.

9.5	No traffic management is to be installed during the times of 0730-0930 and 1530-1900 unless express written permission is given by BCC Highway Network Management

9.6	All scaffolds and mobile working platforms must be within a clearly defined work area and under no circumstances must work be undertaken above live pedestrian or vehicular traffic

9.7	All traffic management must be installed by an operative qualified to Lantra Scheme Sector 12D and their details passed to BCC Highway Network Management prior to works starting on site

Network Management Contact information:

Traffic@bristol.gov.uk

## 10.0	Inspections

10.1	The Authority will carry out onsite inspections and audits on the Contractor and the work carried out, to verify information is correct, check workmanship, verify test certificates and ensure works are being installed/removed in a safe manner.

10.2	The Contractor must submit a programme of works to the Authority prior to any works starting on site and give details of where they will be working, the start time onsite and the time of completion on site and any traffic management requirements.

10.3	The contractor must co-operate fully to any inspections and allow Authority personnel to observe, inspect and in certain circumstances test.

10.4	If for any reason the works programme changes, then the Contractor must advise the authority of the changes at the earliest instance.

10.5	All inspections will be recorded in line with industry and legal recommendations and a copy of the inspection will be available to the Contractor/Duty Holder.

10.6	Inspections will apply to both installation and removal of decorations and any proprietary works that may be required to facilitate the display, such as but limited to new power supplies, new anchor points, Signing and Guarding etc.

10.7	The Authority will offer the Contractor a chance of Joint inspections if required.

10.8	All inspections will be recorded, documented and shared with stakeholders.

## LIST OF APPENDICES

Appendices can be found on Apply for a licence to put up festive lighting over the highway

List Of Appendices

| Appendix “A” | “SL1” Application Form: Word Doc |
| --- | --- |
| Appendix “B” | Example of Licence Format: Word Doc |
| Appendix “C” | Example of Drawings: PDF Doc |
| Appendix “D” | Schedule of Equipment: PDF Doc |
| Appendix “E” | Sample Electrical Test Certificate: PDF Doc |
| Appendix “F” Appendix “G” | Unmetered Supply Information: PDF Doc BCC Meter Administrator PDF & XL Doc Information |